Nephrova Renal Care Pvt. Ltd.

# Incident Report IR-2026-031 — Hadapsar Dialysis Water

Reported by Farah Khan on 21 August 2026. Reviewed by Dr. Sameer Deshpande.

# What happened

The monthly test of RO-H1 product water showed endotoxin exceedance at 0.31 EU/mL (maximum 0.25 EU/mL).

# Immediate actions

Hadapsar ran a reduced schedule and 64 sessions were moved to Kothrud during 21–26 August 2026.

RO-H1 received chemical disinfection and heat disinfection of the loop on 22 August 2026.

All Hadapsar patients dialysed in the week before the result were reviewed by the nephrologist; none had fever or chills during treatment.

# Why it happened

The disinfection of RO-H1 due on 2 August 2026 was missed because the trained technician was on leave and no backup was named. The last disinfection before the result was on 2 July 2026.